## Heat Generators
output | type | energy_carrier | name_old | P_th_cap | P_el_cap | n_th | n_el | IK | OP_fix | OP_var | LT | POT | RF | EL_Cons | tec | MR
output | type | input | name_old | installed capacity (MW_th) | power restriction (MW_el) | efficiency th | efficiency el | investment costs (EUR/MW_th) | OPEX fix (EUR/MWa) | OPEX var (EUR/MWh) | life time | potential restriction (MW_th) | renewable factor | el.Consumption | name | must run [0-1]
heat | boiler | natural gas | boiler1 | 0 | 0 | 1.03 | 0 | 60000 | 2000 | 1.1 | 25 | 0 | 0 | 0.0015 | heat boiler natural gas | 0
heat | boiler | wood chips | boiler2 | 0 | 0 | 0.85 | 0 | 800000 | 0 | 5.4 | 20 | 0 | 1 | 0 | heat boiler wood chips | 0
heat | boiler | wood pellets | boiler3 | 0 | 0 | 0.87 | 0 | 400000 | 0 | 2.7 | 20 | 0 | 1 | 0 | heat boiler wood pellets | 0
heat | boiler | straw | boiler4 | 0 | 0 | 0.85 | 0 | 800000 | 0 | 4 | 20 | 0 | 1 | 0 | heat boiler straw | 0
heat | waste treatment | waste | waste treatment1 | 0 | 0 | 0.98 | 0 | 1200000 | 54000 | 5.6 | 20 | 0 | 0.3 | 0 | heat waste treatment waste | 0
heat | boiler | electricity | boiler5 | 0 | 0 | 0.99 | 0 | 150000 | 1100 | 0.8 | 20 | 0 | 0.5 | 0.005 | heat boiler electricity | 0
heat | comp. heat pump | ambient heat | comp. heat pump2 | 0 | 0 | 3 | 0 | 700000 | 2000 | 8.4 | 25 | 0 | 1 | 0.1 | heat comp. heat pump ambient heat | 0
heat | comp. heat pump | waste heat 20° | comp. heat pump3 | 0 | 0 | 4 | 0 | 700000 | 2000 | 8.4 | 25 | 0 | 1 | 0.1 | heat comp. heat pump waste heat 20° | 0
heat | comp. heat pump | waste heat 40° | comp. heat pump4 | 0 | 0 | 6 | 0 | 700000 | 2000 | 8.4 | 25 | 0 | 1 | 0.1 | heat comp. heat pump waste heat 40° | 0
heat | abs. heat pump | various | abs. heat pump1 | 0 | 0 | 1.7 | 0 | 600000 | 2000 | 0.9 | 25 | 0 | 1 | 0.01 | heat abs. heat pump various | 0
CHP | stirling engine | gas. Biomass | CHP1 | 0 | 0 | 0.58 | 0.2 | 5000000 | 32000 | 26 | 15 | 0 | 1 | 0 | CHP stirling engine gas. Biomass | 0
CHP | steam turbine (medium) | wood chips | CHP2 | 0 | 0 | 0.64 | 0.29 | 4000000 | 29000 | 3.9 | 30 | 0 | 1 | 0 | CHP steam turbine (medium) wood chips | 0
CHP | steam turbine (small) | wood chips | CHP3 | 0 | 0 | 0.62 | 0.25 | 6000000 | 150000 | 0 | 20 | 0 | 1 | 0 | CHP steam turbine (small) wood chips | 0
CHP | steam turbine (medium) | straw | CHP4 | 0 | 0 | 0.64 | 0.29 | 4000000 | 40000 | 6.4 | 25 | 0 | 1 | 0 | CHP steam turbine (medium) straw | 0
CHP | steam turbine (small) | straw | CHP5 | 0 | 0 | 0.62 | 0.3 | 6000000 | 150000 | 0 | 20 | 0 | 1 | 0 | CHP steam turbine (small) straw | 0
CHP | waste treatment | waste | CHP6 | 0 | 0 | 0.62 | 0.24 | 8500000 | 150000 | 0 | 20 | 0 | 0.3 | 0 | CHP waste treatment waste | 0
CHP | spark ignition | natural gas | CHP7 | 0 | 0 | 0.45 | 0.44 | 1000000 | 10000 | 5.4 | 25 | 0 | 0 | 0 | CHP spark ignition natural gas | 0
CHP | spark ignition | gas. Biomass | CHP8 | 0 | 0 | 0.45 | 0.4 | 1000000 | 10000 | 8 | 25 | 0 | 1 | 0 | CHP spark ignition gas. Biomass | 0
CHP | CC gas turbine/ steam extraction turbine | gas/oil | CHP9 | 0 | 0 | 0.35 | 0.55 | 900000 | 30000 | 4.5 | 25 | 0 | 0 | 0 | CHP CC gas turbine/ steam extraction turbine gas/oil | 0
CHP | CC gas turbine/ back-pressure turbine | gas/oil | CHP10 | 0 | 0 | 0.45 | 0.47 | 1300000 | 30000 | 4.5 | 25 | 0 | 0 | 0 | CHP CC gas turbine/ back-pressure turbine gas/oil | 0
heat | Solar Thermal | radiation | Solar Thermal | 0 | 0 | 0.8 | 0 | 550000 | 10000 | 0 | 20 | 0 | 1 | 0 | Solar Thermal | 0

## prices and emmision factors
energy_carrier | energy_carrier_prices | em
energy carrier | prices(EUR/MWh) | emission factor
ambient heat | 0 | 1
electricity | NaN | 0.8
gas. Biomass | 62 | 1
gas/oil | 47 | 0
natural gas | 30 | 0
straw | 22 | 1
various | 20 | 1
waste | 5 | 0.8
waste heat 20° | 0 | 1
waste heat 40° | 0 | 1
wood chips | 22 | 1
wood pellets | 36 | 1
radiation | 0 | 0

## financal and other parameteres
P_co2 | interest_rate | threshold_heatpump | toatl_RF | demand_factor | total_demand
CO2 Price | Interest Rate [0-1] | Threshold Temperature [Celsius] | Total Renewable Factor [0-1] | Demand Scaling Factor [0-1] | Total Demand[ MWh]
25 | 0.5 | 0 | 0 | 1 | 6000000

## Heat Storage
hs_name | cap_hs | unload_cap_hs | load_cap_hs | n_pump_hs | n_turb_hs | IK_cap_hs | IK_pump_hs | OP_fix_hs | LT_hs
name | Storage Capacity [MWh] | maximum unloading power [MW] | maximum loading power [MW] | loading efficiency | unloading efficiency | Invesment costs for additional storage capacity [€/MW] | Invesment costs for additional loading power [€/MW] | OPEX fix [€/MWa] | Life Time [a]
heat storage | 0 | 300 | 300 | 0.95 | 0.98 | 60 | 250 | 10000 | 25

## Techologies
Techologies
heat pump
boiler
CHP
waste treatment
Solar Thermal
Power to Heat
Geo Thermal

## Heat Pump1
heat pump - High Temperature -Geo Thermal (60°C)
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 48.67 | 44.95 | 39.14 | 31.73 | 16.17 | 9.49
45°C | 40.96 | 36.49 | 30.97 | 24.14 | 16.46 | 10.21
50°C | 23.95 | 21.28 | 33.73 | 25.89 | 15 | 10.02
55°C | 0 | 13.11 | 17.41 | 15.05 | 11.67 | 9.04
60°C | 0 | 0 | 7.57 | 8.03 | 8.07 | 7.28
65°C | 0 | 0 | 0 | 5.86 | 4.96 | 4.72
70°C | 0 | 0 | 0 | 0 | 5.33 | 4.31

## Heat Pump2
heat pump - Default
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 5.01 | 4.54 | 4.18 | 3.86 | 3.57 | 3.27
45°C | 4.76 | 4.33 | 3.99 | 3.66 | 3.45 | 3.15
50°C | 4.64 | 4.23 | 3.9 | 3.55 | 3.33 | 3.09
55°C | 0 | 4.08 | 3.71 | 3.42 | 3.2 | 2.98
60°C | 0 | 0 | 3.6 | 3.33 | 3.04 | 2.87
65°C | 0 | 0 | 0 | 3.18 | 2.81 | 2.65
70°C | 0 | 0 | 0 | 0 | 2.8 | 2.46

## Heat Pump3
heat pump - River 5°C
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 3.08 | 2.95 | 2.83 | 2.72 | 2.61 | 2.53
45°C | 2.99 | 2.88 | 2.77 | 2.66 | 2.57 | 2.48
50°C | 2.94 | 2.81 | 2.71 | 2.61 | 2.51 | 2.43
55°C | 0 | 2.75 | 2.64 | 2.54 | 2.45 | 2.38
60°C | 0 | 0 | 2.58 | 2.49 | 2.4 | 2.32
65°C | 0 | 0 | 0 | 2.43 | 2.34 | 2.27
70°C | 0 | 0 | 0 | 0 | 2.29 | 2.22

## Heat Pump4
heat pump - River 10°C
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 3.41 | 3.25 | 3.11 | 2.99 | 2.87 | 2.77
45°C | 3.32 | 3.18 | 3.04 | 2.92 | 2.82 | 2.71
50°C | 3.26 | 3.11 | 2.98 | 2.86 | 2.76 | 2.66
55°C | 0 | 3.04 | 2.91 | 2.8 | 2.7 | 2.6
60°C | 0 | 0 | 2.85 | 2.74 | 2.64 | 2.55
65°C | 0 | 0 | 0 | 2.67 | 2.58 | 2.49
70°C | 0 | 0 | 0 | 0 | 2.52 | 2.43