## Heat Generators
| name | installed capacity (MW_th) | efficiency th | efficiency el | investment costs (EUR/MW_th) | OPEX fix (EUR/MWa) | OPEX var (EUR/MWh) | life time | renewable factor | must run [0-1]
0 | heat boiler natural gas | 2500 | 1.03 | 0 | 60000 | 2000 | 1.1 | 25 | 0 | 0
1 | heat boiler wood chips | 2500 | 0.85 | 0 | 800000 | 0 | 5.4 | 20 | 0.1 | 0
2 | heat boiler wood pellets | 0 | 0.87 | 0 | 400000 | 0 | 2.7 | 20 | 1 | 0
3 | heat boiler straw | 0 | 0.85 | 0 | 800000 | 0 | 4 | 20 | 1 | 0
4 | heat waste treatment waste | 0 | 0.98 | 0 | 1200000 | 54000 | 5.6 | 20 | 0.3 | 0
5 | heat boiler electricity | 0 | 0.99 | 0 | 150000 | 1100 | 0.8 | 20 | 0.5 | 0
6 | heat comp. heat pump ambient heat | 536 | 48.67 | 0 | 700000 | 2000 | 8.4 | 25 | 0 | 1
7 | heat comp. heat pump waste heat 20° | 0 | 4 | 0 | 700000 | 2000 | 8.4 | 25 | 1 | 0
8 | heat comp. heat pump waste heat 40° | 0 | 6 | 0 | 700000 | 2000 | 8.4 | 25 | 1 | 0
9 | heat abs. heat pump various | 0 | 1.7 | 0 | 600000 | 2000 | 0.9 | 25 | 1 | 0
10 | CHP stirling engine gas. Biomass | 0 | 0.58 | 0.2 | 5000000 | 32000 | 26 | 15 | 1 | 0
11 | CHP steam turbine (medium) wood chips | 0 | 0.64 | 0.29 | 4000000 | 29000 | 3.9 | 30 | 1 | 0
12 | CHP steam turbine (small) wood chips | 0 | 0.62 | 0.25 | 6000000 | 150000 | 0 | 20 | 1 | 0
13 | CHP steam turbine (medium) straw | 0 | 0.64 | 0.29 | 4000000 | 40000 | 6.4 | 25 | 1 | 0
14 | CHP steam turbine (small) straw | 0 | 0.62 | 0.3 | 6000000 | 150000 | 0 | 20 | 1 | 0
15 | CHP waste treatment waste | 0 | 0.62 | 0.24 | 8500000 | 150000 | 0 | 20 | 0.3 | 0
16 | CHP spark ignition natural gas | 0 | 0.45 | 0.44 | 1000000 | 10000 | 5.4 | 25 | 0 | 0
17 | CHP spark ignition gas. Biomass | 0 | 0.45 | 0.4 | 1000000 | 10000 | 8 | 25 | 1 | 0
18 | CHP CC gas turbine/ steam extraction turbine gas/oil | 0 | 0.35 | 0.55 | 900000 | 30000 | 4.5 | 25 | 0 | 0
19 | CHP CC gas turbine/ back-pressure turbine gas/oil | 0 | 0.45 | 0.47 | 1300000 | 30000 | 4.5 | 25 | 0 | 0
20 | Solar Thermal | 0 | 0.8 | 0 | 550000 | 10000 | 0 | 20 | 1 | 0
|  | -1898.6716 | Pmax-Pin
|  | 3637.3284 | Pmax

## Energy Carrier
| name | carrier
0 | heat boiler natural gas | natural gas
1 | heat boiler wood chips | wood chips
2 | heat boiler wood pellets | wood pellets
3 | heat boiler straw | straw
4 | heat waste treatment waste | waste
5 | heat boiler electricity | electricity
6 | heat comp. heat pump ambient heat | ambient heat
7 | heat comp. heat pump waste heat 20° | waste heat 20°
8 | heat comp. heat pump waste heat 40° | waste heat 40°
9 | heat abs. heat pump various | various
10 | CHP stirling engine gas. Biomass | gas. Biomass
11 | CHP steam turbine (medium) wood chips | wood chips
12 | CHP steam turbine (small) wood chips | wood chips
13 | CHP steam turbine (medium) straw | straw
14 | CHP steam turbine (small) straw | straw
15 | CHP waste treatment waste | waste
16 | CHP spark ignition natural gas | natural gas
17 | CHP spark ignition gas. Biomass | gas. Biomass
18 | CHP CC gas turbine/ steam extraction turbine gas/oil | gas/oil
19 | CHP CC gas turbine/ back-pressure turbine gas/oil | gas/oil
20 | Solar Thermal | radiation

## prices and emmision factors
| energy carrier | prices(EUR/MWh) | emission factor
0 | ambient heat | 0 | 1
1 | electricity | 20f + 35.05h | 0.8
2 | gas. Biomass | 62 | 1
3 | gas/oil | 47 | 0
4 | natural gas | 30 | 0
5 | straw | 22 | 1
6 | various | 20 | 1
7 | waste | 5 | 0.8
8 | waste heat 20° | 0 | 1
9 | waste heat 40° | 0 | 1
10 | wood chips | 22 | 1
11 | wood pellets | 36 | 1
12 | radiation | 0 | 0

## Data
| CO2 Price | Interest Rate [0-1] | Total Renewable Factor [0-1] | Total Demand[ MWh]
0 | 25 | 0.5 | 0 | 6000000
|  |  | Pmax | 3637.3284

## Heat Storage
| name | Storage Capacity [MWh] | maximum unloading power [MW] | maximum loading power [MW] | loading efficiency | unloading efficiency | Invesment costs for additional storage capacity [€/MW] | Invesment costs for additional loading power [€/MW] | OPEX fix [€/MWa] | Life Time [a]
0 | heat storage | 500 | 600 | 200 | 1 | 1 | 60 | 250 | 10000 | 25

## FiT_Offset
| Radiation | Temperature | Demand | Sale Electricity Price
0 | 0 | 0 | 0 | 0