## Heat Generators
type | tec | energy_carrier | P_th_cap | n_th | n_el | IK | OP_fix | OP_var | c_coldstart | LT | RF | MR | cop_source_sens | cop_inlet_sens | cop_return_sens | source_temp_min | source_temp_fadeout | std_source_temp | std_inlet_temp | std_return_temp | refrigerants | hp_compressor_power | output_power_min_factor | potential | pow_cap | excess_heat_source_price | c_ramp
type | name | input | installed capacity (MW_th) | efficiency th | efficiency el | investment costs (EUR/MW_th) | OPEX fix (EUR/MWa) | OPEX var (EUR/MWh) | Coldstart Costs (EUR/Start) | life time | renewable factor | must run [0-1] | COP source temperature sensitivity (1/°C) | COP flow temperature sensitivity (1/°C) | COP return temperature sensitivity (1/°C) | min shutoff source temperature (°C) | fade out temp where power reduction starts (°C) | Source Temperature (°C) | Nominal Inlet Temperature (°C) | Nominal Return Temperature (°C) | Refrigerants | Maximum Power of the Heatpump Compressor Pel (MW) | Minimum Output Power Factor [0-1] | Maximal Available Potential [MWh] | Maximal Output Power [MW] | Excess Heat Source Price [EUR/MWh] | Ramping Costs [EUR/MWh]
boiler | heat boiler natural gas | natural gas | 0 | 0.97 | 0 | 60000 | 2000 | 1.1 | 1000 | 25 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0
boiler | heat boiler wood chips | wood chips | 0 | 0.85 | 0 | 800000 | 0 | 5.4 | 1000 | 20 | 1 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0
boiler | heat boiler wood pellets | wood pellets | 0 | 0.87 | 0 | 400000 | 0 | 2.7 | 1000 | 20 | 1 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0
boiler | heat boiler straw | straw | 0 | 0.85 | 0 | 800000 | 0 | 4 | 1000 | 20 | 1 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0
waste treatment | heat waste treatment waste | waste | 0 | 0.98 | 0 | 1200000 | 54000 | 5.6 | 1000 | 20 | 0.3 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 100
boiler | heat boiler electricity | electricity | 0 | 0.99 | 0 | 150000 | 1100 | 0.8 | 1000 | 20 | 0.5 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0
CHP-BP | CHP-BP stirling engine gas. Biomass | gas. Biomass | 0 | 0.58 | 0.2 | 5000000 | 32000 | 26 | 1000 | 15 | 1 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 100
CHP-SE | CHP-SE steam turbine (medium) wood chips | wood chips | 0 | 0.64 | 0.29 | 4000000 | 29000 | 3.9 | 1000 | 30 | 1 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 100
CHP-SE | CHP-SE steam turbine (small) wood chips | wood chips | 0 | 0.62 | 0.25 | 6000000 | 150000 | 0 | 1000 | 20 | 1 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 100
CHP-SE | CHP-SE steam turbine (medium) straw | straw | 0 | 0.64 | 0.29 | 4000000 | 40000 | 6.4 | 1000 | 25 | 1 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 100
CHP-SE | CHP-SE steam turbine (small) straw | straw | 0 | 0.62 | 0.3 | 6000000 | 150000 | 0 | 1000 | 20 | 1 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 100
CHP-SE | CHP-SE waste treatment waste | waste | 0 | 0.62 | 0.24 | 8500000 | 150000 | 0 | 1000 | 20 | 0.3 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 100
CHP-BP | CHP-BP spark ignition natural gas | natural gas | 0 | 0.45 | 0.44 | 1000000 | 10000 | 5.4 | 1000 | 25 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 100
CHP-BP | CHP-BP spark ignition gas. Biomass | gas. Biomass | 0 | 0.45 | 0.4 | 1000000 | 10000 | 8 | 1000 | 25 | 1 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 100
CHP-SE | CHP-SE CC gas turbine/ steam extraction turbine gas/oil | gas/oil | 0 | 0.35 | 0.55 | 900000 | 30000 | 4.5 | 1000 | 25 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 100
CHP-BP | CHP-BP CC gas turbine/ back-pressure turbine gas/oil | gas/oil | 0 | 0.45 | 0.47 | 1300000 | 30000 | 4.5 | 1000 | 25 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 100
Solar Thermal | Solar Thermal | radiation | 0 | 0.8 | 0 | 550000 | 10000 | 0 | 1000 | 20 | 1 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0
heat pump | Heat Pump Geothermal | electricity | 0 | 3.5 | 0 | 300000 | 2000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 60 | 95 | 70 | R718 (Water) |  | 0 | 0 | 0 | 0 | 0
heat pump | Heat Pump Default | electricity | 0 | 3 | 0 | 700000 | 2000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 15 | 95 | 70 | R134a |  | 0 | 0 | 0 | 0 | 0
heat pump | Heat Pump River | electricity | 0 | 4 | 0 | 700000 | 3000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 10 | 95 | 70 | R718 (Water) |  | 0 | 0 | 0 | 0 | 0
Heat Pump Ind. Wasteheat | Heat Pump Ind. Wasteheat | electricity | 0 | 5 | 0 | 350000 | 3000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | [5 empty] | 0 | 0 | 0 | 0 | 0
Heat Pump River Water | Heat Pump River Water - Ammoniak | electricity | 0 | 3.41 | 0 | 700000 | 2000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 10 | 70 | 40 | Ammoniak |  | 0 | 0 | 0 | 0 | 0
Heat Pump River Water | Heat Pump River Water - n-Butan | electricity | 0 | 2.57 | 0 | 500000 | 2000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 10 | 80 | 50 | n-Butan |  | 0 | 0 | 0 | 0 | 0
Heat Pump River Water | Heat Pump River Water - CO2 | electricity | 0 | 2 | 0 | 400000 | 2000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 10 | 80 | 50 | CO2 |  | 0 | 0 | 0 | 0 | 0
Heat Pump Wastewater | Heat Pump Wastewater - Ammoniak | electricity | 0 | 3.41 | 0 | 770000 | 2000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 10 | 70 | 40 | Ammoniak |  | 0 | 0 | 0 | 0 | 0
Heat Pump Wastewater | Heat Pump Wastewater - n-Butan | electricity | 0 | 2.57 | 0 | 550000 | 2000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 10 | 80 | 50 | n-Butan |  | 0 | 0 | 0 | 0 | 0
Heat Pump Wastewater | Heat Pump Wastewater - CO2 | electricity | 0 | 2 | 0 | 440000 | 2000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 10 | 80 | 50 | CO2 |  | 0 | 0 | 0 | 0 | 0
Heat Pump Air | Heat Pump Air - Ammoniak | electricity | 0 | 3.41 | 0 | 777000 | 2000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | -20 | -10 | 10 | 70 | 40 | Ammoniak |  | 0 | 0 | 0 | 0 | 0
Heat Pump Air | Heat Pump Air - n-Butan | electricity | 0 | 2.57 | 0 | 555000 | 2000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | -20 | -10 | 10 | 80 | 50 | n-Butan |  | 0 | 0 | 0 | 0 | 0
Heat Pump Air | Heat Pump Air - CO2 | electricity | 0 | 2 | 0 | 444000 | 2000 | 8.4 | 1000 | 25 | 0 | 0 | 0 | 0 | 0 | -20 | -10 | 10 | 80 | 50 | CO2 |  | 0 | 0 | 0 | 0 | 0

## prices and emmision factors
energy_carrier | energy_carrier_prices | em
energy carrier | prices(EUR/MWh) | emission factor [tCO2/MWh]
ambient heat | 0 | 1
electricity | NaN | 0.8
CHP gas | 62 | 1
gas/oil | 47 | 0
natural gas | 30 | 1
straw | 22 | 1
various | 20 | 1
waste | 5 | 0.8
waste heat 20° | 0 | 1
waste heat 40° | 0 | 1
wood chips | 22 | 1
wood pellets | 36 | 1
radiation | 0 | 0

## financal and other parameteres
P_co2 | interest_rate | threshold_heatpump | toatl_RF | demand_factor | total_demand
CO2 Price [EUR/tC02] | Interest Rate [0-1] | Threshold Temperature [Celsius] | Minimum Renewable Factor [0-1] | Demand Scaling Factor [0-1] | Total Demand[ MWh]
25 | 0.05 | -20 | 0 | 1 | 1763143

## Heat Storage
hs_name | cap_hs | cap_losse_hs | unload_cap_hs | load_cap_hs | n_pump_hs | n_turb_hs | IK_cap_hs | OP_fix_hs | LT_hs
name | Storage Capacity [MWh] | Hourly Stoarge Losses [%] | maximum unloading power [MW] | maximum loading power [MW] | loading efficiency | unloading efficiency | Invesment costs for additional storage capacity [€/MWh] | OPEX fix [€/MWh] | Life Time [a]
default heat storage | 0 | 1 | 80 | 80 | 0.95 | 0.95 | 60 | 10000 | 25

## Techologies
Techologies
heat pump
boiler
CHP-SE
CHP-BP
waste treatment
Solar Thermal
Power To Heat
Waste Heat
Geo Thermal
Heat Pump Air
Heat Pump River Water
Heat Pump Wastewater
Heat Pump Ind. Wasteheat

## Heat Pump1
R718 (Water) | heat pump | Source Tempearture: | 60°C
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 48.67 | 44.95 | 39.14 | 31.73 | 16.17 | 9.49
45°C | 40.96 | 36.49 | 30.97 | 24.14 | 16.46 | 10.21
50°C | 23.95 | 21.28 | 33.73 | 25.89 | 15 | 10.02
55°C | 0 | 13.11 | 17.41 | 15.05 | 11.67 | 9.04
60°C | 0 | 0 | 7.57 | 8.03 | 8.07 | 7.28
65°C | 0 | 0 | 0 | 5.86 | 4.96 | 4.72
70°C | 0 | 0 | 0 | 0 | 5.33 | 4.31

## Heat Pump2
R134a | heat pump | Source Tempearture: | 15°C
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 5.01 | 4.54 | 4.18 | 3.86 | 3.57 | 3.27
45°C | 4.76 | 4.33 | 3.99 | 3.66 | 3.45 | 3.15
50°C | 4.64 | 4.23 | 3.9 | 3.55 | 3.33 | 3.09
55°C | 0 | 4.08 | 3.71 | 3.42 | 3.2 | 2.98
60°C | 0 | 0 | 3.6 | 3.33 | 3.04 | 2.87
65°C | 0 | 0 | 0 | 3.18 | 2.81 | 2.65
70°C | 0 | 0 | 0 | 0 | 2.8 | 2.46

## Heat Pump3
R718 (Water) | heat pump | Source Tempearture: | 5°C
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 3.08 | 2.95 | 2.83 | 2.72 | 2.61 | 2.53
45°C | 2.99 | 2.88 | 2.77 | 2.66 | 2.57 | 2.48
50°C | 2.94 | 2.81 | 2.71 | 2.61 | 2.51 | 2.43
55°C | 0 | 2.75 | 2.64 | 2.54 | 2.45 | 2.38
60°C | 0 | 0 | 2.58 | 2.49 | 2.4 | 2.32
65°C | 0 | 0 | 0 | 2.43 | 2.34 | 2.27
70°C | 0 | 0 | 0 | 0 | 2.29 | 2.22

## Heat Pump4
R718 (Water) | heat pump | Source Tempearture: | 10°C
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 3.41 | 3.25 | 3.11 | 2.99 | 2.87 | 2.77
45°C | 3.32 | 3.18 | 3.04 | 2.92 | 2.82 | 2.71
50°C | 3.26 | 3.11 | 2.98 | 2.86 | 2.76 | 2.66
55°C | 0 | 3.04 | 2.91 | 2.8 | 2.7 | 2.6
60°C | 0 | 0 | 2.85 | 2.74 | 2.64 | 2.55
65°C | 0 | 0 | 0 | 2.67 | 2.58 | 2.49
70°C | 0 | 0 | 0 | 0 | 2.52 | 2.43

## Heat Pump5
Ammoniak | Heat Pump River Water | Source Tempearture: | 10°C
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 3.41 | 3.25 | 3.11 | 2.99 | 2.87 | 2.77
45°C | 3.32 | 3.18 | 3.04 | 2.92 | 2.82 | 2.71
50°C | 3.26 | 3.11 | 2.98 | 2.86 | 2.76 | 2.66
55°C | 0 | 3.04 | 2.91 | 2.8 | 2.7 | 2.6
60°C | 0 | 0 | 2.85 | 2.74 | 2.64 | 2.55
65°C | 0 | 0 | 0 | 2.67 | 2.58 | 2.49
70°C | 0 | 0 | 0 | 0 | 2.52 | 2.43

## Heat Pump6
n-Butan | Heat Pump River Water | Source Tempearture: | 10°C
COP | 80°C | 90°C | 100°C | 110°C | 120°C
50°C | 2.57 | 2.4 | 2.24 | 2.11 | 1.99
55°C | 2.53 | 2.35 | 2.21 | 2.08 | 1.96
60°C | 2.48 | 2.31 | 2.17 | 2.04 | 1.93

## Heat Pump7
CO2 | Heat Pump River Water | Source Tempearture: | 10°C
COP | 80°C | 85°C | 90°C | 95°C
50°C | 2 | 1.98 | 1.96 | 1.94
55°C | 1.83 | 1.82 | 1.81 | 1.8
60°C | 1.68 | 1.68 | 1.67 | 1.67

## Heat Pump8
Ammoniak | Heat Pump Wastewater | Source Tempearture: | 10°C
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 3.41 | 3.25 | 3.11 | 2.99 | 2.87 | 2.77
45°C | 3.32 | 3.18 | 3.04 | 2.92 | 2.82 | 2.71
50°C | 3.26 | 3.11 | 2.98 | 2.86 | 2.76 | 2.66
55°C | 0 | 3.04 | 2.91 | 2.8 | 2.7 | 2.6
60°C | 0 | 0 | 2.85 | 2.74 | 2.64 | 2.55
65°C | 0 | 0 | 0 | 2.67 | 2.58 | 2.49
70°C | 0 | 0 | 0 | 0 | 2.52 | 2.43

## Heat Pump9
n-Butan | Heat Pump Wastewater | Source Tempearture: | 10°C
COP | 80°C | 90°C | 100°C | 110°C | 120°C
50°C | 2.57 | 2.4 | 2.24 | 2.11 | 1.99
55°C | 2.53 | 2.35 | 2.21 | 2.08 | 1.96
60°C | 2.48 | 2.31 | 2.17 | 2.04 | 1.93

## Heat Pump10
CO2 | Heat Pump Wastewater | Source Tempearture: | 10°C
COP | 80°C | 85°C | 90°C | 95°C
50°C | 2 | 1.98 | 1.96 | 1.94
55°C | 1.83 | 1.82 | 1.81 | 1.8
60°C | 1.68 | 1.68 | 1.67 | 1.67

## Heat Pump11
Ammoniak | Heat Pump Air | Source Tempearture: | 10°C
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 3.41 | 3.25 | 3.11 | 2.99 | 2.87 | 2.77
45°C | 3.32 | 3.18 | 3.04 | 2.92 | 2.82 | 2.71
50°C | 3.26 | 3.11 | 2.98 | 2.86 | 2.76 | 2.66
55°C | 0 | 3.04 | 2.91 | 2.8 | 2.7 | 2.6
60°C | 0 | 0 | 2.85 | 2.74 | 2.64 | 2.55
65°C | 0 | 0 | 0 | 2.67 | 2.58 | 2.49
70°C | 0 | 0 | 0 | 0 | 2.52 | 2.43

## Heat Pump12
n-Butan | Heat Pump Air | Source Tempearture: | 10°C
COP | 80°C | 90°C | 100°C | 110°C | 120°C
50°C | 2.57 | 2.4 | 2.24 | 2.11 | 1.99
55°C | 2.53 | 2.35 | 2.21 | 2.08 | 1.96
60°C | 2.48 | 2.31 | 2.17 | 2.04 | 1.93

## Heat Pump13
CO2 | Heat Pump Air | Source Tempearture: | 10°C
COP | 80°C | 85°C | 90°C | 95°C
50°C | 2 | 1.98 | 1.96 | 1.94
55°C | 1.83 | 1.82 | 1.81 | 1.8
60°C | 1.68 | 1.68 | 1.67 | 1.67