## Heat Generators
name | type | energy_carrier | P_th_cap | n_th | n_el | IK | OP_fix | OP_var | LT | RF | MR | c_ramp | P_max_el_j
name | type | input | installed capacity (MW_th) | efficiency th | efficiency el | investment costs (EUR/MW_th) | OPEX fix (EUR/MWa) | OPEX var (EUR/MWh) | life time | renewable factor | must run [0-1] | Ramping Costs [EUR/MWh] | P_max in condensing mode [MWel]
heat boiler natural gas | boiler | natural gas | 0 | 0.9 | 0 | 100000 | 4000 | 0.5 | 25 | 0 | 0 | 0 | 0
heat boiler wood chips | boiler | wood chips | 0 | 0.85 | 0 | 670000 | 13000 | 2.9 | 20 | 0 | 0 | 0 | 0
heat boiler wood pellets | boiler | wood pellets | 0 | 0.87 | 0 | 700000 | 13000 | 3 | 20 | 0 | 0 | 0 | 0
heat boiler straw | boiler | straw | 0 | 0.83 | 0 | 750000 | 13000 | 3.1 | 20 | 0 | 0 | 0 | 0
waste inceneration plant | boiler | waste | 0 | 0.81 | 0 | 1200000 | 230000 | 0.5 | 20 | 0 | 0 | 0 | 0
heat boiler electricity | boiler | electricity | 0 | 0.99 | 0 | 150000 | 2000 | 0.5 | 20 | 0 | 0 | 0 | 0
Geothermal High Temperature | boiler | various | 0 | 0 | 0 | 1600000 | 35000 | 0 | 30 | 0 | 0 | 0 | 0
Gas turbine | CHP-SE | natural gas | 0 | 0.46 | 0.37 | 875000 | 23000 | 1.7 | 25 | 0 | 0 | 100 | 0
CC gas turbine/ steam extraction turbine | CHP-SE | natural gas | 0 | 0.35 | 0.5 | 1500000 | 34000 | 4.6 | 25 | 0 | 0 | 100 | 0
CC gas turbine/ back-pressure turbine | CHP-BP | natural gas | 0 | 0.36 | 0.5 | 1300000 | 34000 | 4.5 | 25 | 0 | 0 | 100 | 0
Default Solar Thermal | Solar Thermal | radiation | 0 | 0.8 | 0 | 550000 | 10000 | 0.5 | 20 | 0 | 0 | 0 | 0
Heat Pump (Geothermal 80°C) | heat pump | electricity | 0 | 4 | 0 | 510000 | 10000 | 0.5 | 25 | 0 | 0 | 0 | 0
Heat Pump (Geothermal 60°C) | heat pump | electricity | 0 | 4 | 0 | 510000 | 10000 | 0.5 | 25 | 0 | 0 | 0 | 0
Heat Pump (River 10°C) | heat pump | electricity | 0 | 4 | 0 | 510000 | 10000 | 0.5 | 25 | 0 | 0 | 0 | 0
Heat Pump (River 5°C) | heat pump | electricity | 0 | 4 | 0 | 510000 | 10000 | 0.5 | 25 | 0 | 0 | 0 | 0
Default Waste Inceneration Plant | waste treatment | waste | 0 | 0.75 | 0 | 1200000 | 54000 | 5.6 | 20 | 0 | 0 | 100 | 0
Default Power to Heat Plant | Power To Heat | electricity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Excess Heat Plant | Waste Heat | various 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Geothermal Plant | Geo Thermal | various 2 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHP-SE steam turbine (medium) wood chips | CHP-SE | wood chips | 0 | 0.64 | 0.29 | 4000000 | 29000 | 3.9 | 30 | 0 | 0 | 100 | 0
CHP-SE steam turbine (small) wood chips | CHP-SE | wood chips | 0 | 0.62 | 0.25 | 6000000 | 150000 | 0 | 20 | 0 | 0 | 100 | 0
CHP-SE steam turbine (medium) straw | CHP-SE | straw | 0 | 0.64 | 0.29 | 4000000 | 40000 | 6.4 | 25 | 0 | 0 | 100 | 0
CHP-SE steam turbine (small) straw | CHP-SE | straw | 0 | 0.62 | 0.3 | 6000000 | 150000 | 0 | 20 | 0 | 0 | 100 | 0
CHP-SE waste treatment waste | CHP-SE | waste | 0 | 0.62 | 0.24 | 8500000 | 150000 | 0 | 20 | 0 | 0 | 100 | 0
CHP-BP stirling engine gas. Biomass | CHP-BP | biogas | 0 | 0.58 | 0.2 | 5000000 | 32000 | 26 | 15 | 0 | 0 | 100 | 0
CHP-BP spark ignition natural gas | CHP-BP | natural gas | 0 | 0.45 | 0.44 | 1000000 | 10000 | 5.4 | 25 | 0 | 0 | 100 | 0
CHP-BP spark ignition gas. Biomass | CHP-BP | biogas | 0 | 0.45 | 0.4 | 1000000 | 10000 | 8 | 25 | 0 | 0 | 100 | 0

## prices and emmision factors
energy_carrier | energy_carrier_prices | em
energy carrier | prices(EUR/MWh) | emission factor [tCO2/MWh]
electricity | NaN | 0.8
biogas | 100 | 0
oil | 55.4 | 0.28
natural gas | 29.8 | 0.2
hard coal | 7.7 | 0.34
waste | 1 | 0.05
wood chips | 22 | 0
wood pellets | 36 | 0
biomass | 62 | 0
straw | 22 | 0
radiation | 0 | 0
various 1 | 0 | 0
various 2 | 0 | 0
various 3 | 0 | 0
various 4 | 0 | 0
various 5 | 0 | 0

## financal and other parameteres
P_co2 | interest_rate | threshold_heatpump | toatl_RF | demand_factor | total_demand
CO2 Price [EUR/tC02] | Interest Rate [0-1] | Threshold Temperature [Celsius] | Minimum Renewable Factor [0-1] | Demand Scaling Factor [0-1] | Total Demand[ MWh]
25 | 0.05 | -20 | 0 | 1 | 6000000

## Heat Storage
hs_name | cap_hs | cap_losse_hs | unload_cap_hs | load_cap_hs | n_pump_hs | IK_cap_hs | OP_fix_hs | LT_hs
name | Storage Capacity [MWh] | Hourly Stoarge Losses [%] | maximum unloading power [MW] | maximum loading power [MW] | loading efficiency | Invesment costs for additional storage capacity [€/MWh] | OPEX fix [€/MWh] | Life Time [a]
default heat storage | 0 | 1 | 0 | 0 | 0.95 | 5000 | 100 | 25

## Technologies
Technologies | Name
heat pump | Heat Pump
boiler | Heat Only Boiler
CHP-SE | CHP Steam Extraction
CHP-BP | CHP Back Pressure
waste treatment | Waste Inceneration Plants
Solar Thermal | Soloar Thermal Plants
Power To Heat | Power to heat plants
Waste Heat | Excess Heat Plants
Geo Thermal | Geothermal Plants

## Heat Pump1
heat pump # Heat Pump (Geothermal 80°C)
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 48.67 | 44.95 | 39.14 | 31.73 | 16.17 | 9.49
45°C | 40.96 | 36.49 | 30.97 | 24.14 | 16.46 | 10.21
50°C | 23.95 | 21.28 | 33.73 | 25.89 | 15 | 10.02
55°C | 0 | 13.11 | 17.41 | 15.05 | 11.67 | 9.04
60°C | 0 | 0 | 7.57 | 8.03 | 8.07 | 7.28
65°C | 0 | 0 | 0 | 5.86 | 4.96 | 4.72
70°C | 0 | 0 | 0 | 0 | 5.33 | 4.31

## Heat Pump2
heat pump # Heat Pump (Geothermal 60°C)
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 5.01 | 4.54 | 4.18 | 3.86 | 3.57 | 3.27
45°C | 4.76 | 4.33 | 3.99 | 3.66 | 3.45 | 3.15
50°C | 4.64 | 4.23 | 3.9 | 3.55 | 3.33 | 3.09
55°C | 0 | 4.08 | 3.71 | 3.42 | 3.2 | 2.98
60°C | 0 | 0 | 3.6 | 3.33 | 3.04 | 2.87
65°C | 0 | 0 | 0 | 3.18 | 2.81 | 2.65
70°C | 0 | 0 | 0 | 0 | 2.8 | 2.46

## Heat Pump3
heat pump # Heat Pump (River 5°C)
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 3.08 | 2.95 | 2.83 | 2.72 | 2.61 | 2.53
45°C | 2.99 | 2.88 | 2.77 | 2.66 | 2.57 | 2.48
50°C | 2.94 | 2.81 | 2.71 | 2.61 | 2.51 | 2.43
55°C | 0 | 2.75 | 2.64 | 2.54 | 2.45 | 2.38
60°C | 0 | 0 | 2.58 | 2.49 | 2.4 | 2.32
65°C | 0 | 0 | 0 | 2.43 | 2.34 | 2.27
70°C | 0 | 0 | 0 | 0 | 2.29 | 2.22

## Heat Pump4
heat pump # Heat Pump (River 10°C)
COP | 70°C | 75°C | 80°C | 85°C | 90°C | 95°C
40°C | 3.41 | 3.25 | 3.11 | 2.99 | 2.87 | 2.77
45°C | 3.32 | 3.18 | 3.04 | 2.92 | 2.82 | 2.71
50°C | 3.26 | 3.11 | 2.98 | 2.86 | 2.76 | 2.66
55°C | 0 | 3.04 | 2.91 | 2.8 | 2.7 | 2.6
60°C | 0 | 0 | 2.85 | 2.74 | 2.64 | 2.55
65°C | 0 | 0 | 0 | 2.67 | 2.58 | 2.49
70°C | 0 | 0 | 0 | 0 | 2.52 | 2.43

## CHP-SE
CHP-SE#Default
name | Pmax_el
CC gas turbine/ steam extraction turbine | 0